## PIPESEAL SIZING
|  | PIPESEAL SIZING | [5 empty] | 1 | 0.5
[8 empty] | 1.25 | 0.75
|  | INPUT |  | OUTPUT |  |  |  | 1.5 | 1
|  | PIPE OD | HOLE ID | MODEL | NO. OF LINKS |  |  | 2 | 2
|  | 4.5 | 6.065 | PS 300 | 10 |  |  | 2.5 | 2.5
[8 empty] | 3 | 3
[8 empty] | 3.5 | 4
[8 empty] | 4 | 5
[8 empty] | 5 | 6
8
|  | Input the pipe ODs and the penetration hole IDs to output seal models and # of links. | [6 empty] | 10
12
14
15
16
18
CHECK SLEEVE IDs? |  |  | CHECK PIPE ODs? | [5 empty] | 20
22
INPUT | OUTPUT |  | INPUT | OUTPUT |  |  |  |  | 24
NOMINAL DIA | STEEL SLEEVE ID |  | NOMINAL DIA | STEEL/PVC OD | CAST IRON (EX HEAVY) OD | CAST IRON (SERV WT) OD | DUCTILE IRON OD |  | 26
6 | 6.065 |  | 4 | 4.5 | 4.5 | 4.3 | 4.8 |  | 28
30
32
34
36
54
Input nominal sleeve diameters to output sleeve IDs. |  |  | Input nominal pipe diameters to output pipe ODs used in sizing. | [5 empty] | 42
48
54
Rev. 5
FLEXICRAFT INDUSTRIES CHICAGO, IL 312-738-3588 sales@flexicraft.com | [6 empty] | www.flexicraft.com

## TABLES & DETAILS (hidden)
PENETRATION DETAILS | [5 empty] | PRIMARY CHOICE | [7 empty] | ALTERNATE 1 CHOICE | [7 empty] | ALTERNATE 2 CHOICE | [7 empty] | FINAL CHOICE
PIPE OD | PEN ID | ANLR SPACE | BOLT CIRCLE |  |  | CHORD L | MODEL | % RANGE | RAW # | # | MIN LINK CHK | OD RANGE CHK | FINAL CHECK | CHORD L | MODEL | % RANGE | RAW # | # | MIN LINK CHK | OD RANGE CHK | FINAL CHECK | CHORD L | MODEL | % RANGE | RAW # | # | MIN LINK CHK | OD RANGE CHK | FINAL CHECK | CHORD L | MODEL | % RANGE | #
4.5 | 6.065 | 0.78 | 5.2825 |  |  | 1.51 | PS 300 | 33.33% | 10.9848 | 10 | OK | OK | OK | 0.906 | PS 275 | 88.89% | 18.308 | 18 | OK | OK | OK | 0.906 | PS 275 | 88.89% | 18.308 | 18 | OK | OK | OK | 1.51 | PS 300 | 33.33% | 10
[10 empty] | round up <0.90 | [7 empty] | round up <0.90 | [7 empty] | round up <0.90
[10 empty] | if int raw<10 | [7 empty] | if int raw<10 | [7 empty] | if int raw<10
[34 empty] | PRIMARY CHOICE |  |  |  | ALTERNATE 1 CHOICE |  |  |  | ALTERNATE 2 CHOICE
[34 empty] | ANLR SPACE | MODEL | CHORD LENGTH | % RANGE | ANLR SPACE | MODEL | CHORD LENGTH | % RANGE | ANLR SPACE | MODEL | CHORD LENGTH | % RANGE
MODEL INFORMATION | [33 empty] | 0.5 | PS 200 | 1.12 | 0% | 0.5 | PS 200 | 1.12 | 0% | 0.5 | PS 200 | 1.12 | 0%
MODEL | FREE THK | EXP THK | CHORD L | . | RANGE | pipe min OD | Pipe max OD | min # links | [25 empty] | 0.51 | PS 200 | 1.12 | 7.143% | 0.51 | PS 200 | 1.12 | 7.143% | 0.51 | PS 200 | 1.12 | 7.143%
PS 200 | 0.5 | 0.64 | 1.12 | . | 0.14 | 0.83858 | 12.7519 | 4 | [25 empty] | 0.52 | PS 200 | 1.12 | 14.29% | 0.52 | PS 200 | 1.12 | 14.29% | 0.52 | PS 200 | 1.12 | 14.29%
PS 275 | 0.62 | 0.8 | 0.906 | . | 0.18 | 0 | 3.5433 | 4 | [25 empty] | 0.53 | PS 200 | 1.12 | 21.43% | 0.53 | PS 200 | 1.12 | 21.43% | 0.53 | PS 200 | 1.12 | 21.43%
PS 300 | 0.71 | 0.92 | 1.51 | . | 0.21 | 1.752 | 9.8425 | 5 | [25 empty] | 0.54 | PS 200 | 1.12 | 28.57% | 0.54 | PS 200 | 1.12 | 28.57% | 0.54 | PS 200 | 1.12 | 28.57%
PS 315 | 0.82 | 1.1 | 1.469 | . | 0.28 | 1.4567 | 12.4015 | 5 | [25 empty] | 0.55 | PS 200 | 1.12 | 35.71% | 0.55 | PS 200 | 1.12 | 35.71% | 0.55 | PS 200 | 1.12 | 35.71%
PS 325 | 0.94 | 1.14 | 3.11 | . | 0.2 | 5.2362 | 27.992 | 6 | [25 empty] | 0.56 | PS 200 | 1.12 | 42.86% | 0.56 | PS 200 | 1.12 | 42.86% | 0.56 | PS 200 | 1.12 | 42.86%
PS 340 | 1.05 | 1.33 | 1.57 | . | 0.28 | 0.55118 | 12.7519 | 4 | [25 empty] | 0.57 | PS 200 | 1.12 | 50% | 0.57 | PS 200 | 1.12 | 50% | 0.57 | PS 200 | 1.12 | 50%
PS 360 | 1.29 | 1.65 | 2.106 | . | 0.36 | 1.5748 | 16 | 5 | [25 empty] | 0.58 | PS 200 | 1.12 | 57.14% | 0.58 | PS 200 | 1.12 | 57.14% | 0.58 | PS 200 | 1.12 | 57.14%
PS 400 | 1.43 | 1.87 | 3.622 | . | 0.44 | 5.5 | 48.0314 | 6 | [25 empty] | 0.59 | PS 200 | 1.12 | 64.29% | 0.59 | PS 200 | 1.12 | 64.29% | 0.59 | PS 200 | 1.12 | 64.29%
PS 410 | 1.48 | 1.91 | 2.598 | . | 0.43 | 2.374 | 12.7519 | 5 | [25 empty] | 0.6 | PS 200 | 1.12 | 71.43% | 0.6 | PS 200 | 1.12 | 71.43% | 0.6 | PS 200 | 1.12 | 71.43%
PS 425 | 1.13 | 1.43 | 3.622 | . | 0.3 | 5.6693 | 48.0314 | 6 | [25 empty] | 0.61 | PS 200 | 1.12 | 78.57% | 0.61 | PS 200 | 1.12 | 78.57% | 0.61 | PS 200 | 1.12 | 78.57%
PS 475 | 1.62 | 2.08 | 2.63 | . | 0.46 | 2.374 | 48.0314 | 5 | [25 empty] | 0.62 | PS 275 | 0.906 | 0% | 0.62 | PS 275 | 0.906 | 0% | 0.62 | PS 275 | 0.906 | 0%
PS 500 | 2.37 | 2.81 | 3.86 | . | 0.44 | 3.937 | 48.0314 | 5 | [25 empty] | 0.63 | PS 275 | 0.906 | 5.556% | 0.63 | PS 275 | 0.906 | 5.556% | 0.63 | PS 275 | 0.906 | 5.556%
PS 525 | 2.18 | 2.58 | 3.86 | . | 0.4 | 5.2362 | 48.0314 | 6 | [25 empty] | 0.64 | PS 275 | 0.906 | 11.11% | 0.64 | PS 275 | 0.906 | 11.11% | 0.64 | PS 275 | 0.906 | 11.11%
PS 575 | 1.88 | 2.35 | 3.1 | . | 0.47 | 5.1181 | 48.0314 | 5 | [25 empty] | 0.65 | PS 275 | 0.906 | 16.67% | 0.65 | PS 275 | 0.906 | 16.67% | 0.65 | PS 275 | 0.906 | 16.67%
PS 600 | 3.2 | 4 | 6 | . | 0.8 | 12 | 72 | 6 | [25 empty] | 0.66 | PS 275 | 0.906 | 22.22% | 0.66 | PS 275 | 0.906 | 22.22% | 0.66 | PS 275 | 0.906 | 22.22%
[34 empty] | 0.67 | PS 275 | 0.906 | 27.78% | 0.67 | PS 275 | 0.906 | 27.78% | 0.67 | PS 275 | 0.906 | 27.78%
[34 empty] | 0.68 | PS 275 | 0.906 | 33.33% | 0.68 | PS 275 | 0.906 | 33.33% | 0.68 | PS 275 | 0.906 | 33.33%
[34 empty] | 0.69 | PS 275 | 0.906 | 38.89% | 0.69 | PS 275 | 0.906 | 38.89% | 0.69 | PS 275 | 0.906 | 38.89%
[34 empty] | 0.7 | PS 275 | 0.906 | 44.44% | 0.7 | PS 275 | 0.906 | 44.44% | 0.7 | PS 275 | 0.906 | 44.44%
[34 empty] | 0.71 | PS 300 | 1.51 | 0% | 0.71 | PS 275 | 0.906 | 50% | 0.71 | PS 275 | 0.906 | 50%
[34 empty] | 0.72 | PS 300 | 1.51 | 4.762% | 0.72 | PS 275 | 0.906 | 55.56% | 0.72 | PS 275 | 0.906 | 55.56%
[34 empty] | 0.73 | PS 300 | 1.51 | 9.524% | 0.73 | PS 275 | 0.906 | 61.11% | 0.73 | PS 275 | 0.906 | 61.11%
[34 empty] | 0.74 | PS 300 | 1.51 | 14.29% | 0.74 | PS 275 | 0.906 | 66.67% | 0.74 | PS 275 | 0.906 | 66.67%
[34 empty] | 0.75 | PS 300 | 1.51 | 19.05% | 0.75 | PS 275 | 0.906 | 72.22% | 0.75 | PS 275 | 0.906 | 72.22%
[34 empty] | 0.76 | PS 300 | 1.51 | 23.81% | 0.76 | PS 275 | 0.906 | 77.78% | 0.76 | PS 275 | 0.906 | 77.78%
[34 empty] | 0.77 | PS 300 | 1.51 | 28.57% | 0.77 | PS 275 | 0.906 | 83.33% | 0.77 | PS 275 | 0.906 | 83.33%
[34 empty] | 0.78 | PS 300 | 1.51 | 33.33% | 0.78 | PS 275 | 0.906 | 88.89% | 0.78 | PS 275 | 0.906 | 88.89%
[34 empty] | 0.79 | PS 300 | 1.51 | 38.1% | 0.79 | PS 275 | 0.906 | 94.44% | 0.79 | PS 275 | 0.906 | 94.44%
[34 empty] | 0.8 | PS 300 | 1.51 | 42.86% | 0.8 | PS 275 | 0.906 | 100% | 0.8 | PS 275 | 0.906 | 100%
[34 empty] | 0.81 | PS 300 | 1.51 | 47.62% | 0.81 | PS 300 | 1.51 | 47.62% | 0.81 | PS 300 | 1.51 | 47.62%
[34 empty] | 0.82 | PS 300 | 1.51 | 52.38% | 0.82 | PS 315 | 1.469 | 0% | 0.82 | PS 315 | 1.469 | 0%
[34 empty] | 0.83 | PS 315 | 1.469 | 3.571% | 0.83 | PS 315 | 1.469 | 3.571% | 0.83 | PS 315 | 1.469 | 3.571%
[34 empty] | 0.84 | PS 315 | 1.469 | 7.143% | 0.84 | PS 315 | 1.469 | 7.143% | 0.84 | PS 315 | 1.469 | 7.143%
[34 empty] | 0.85 | PS 315 | 1.469 | 10.71% | 0.85 | PS 315 | 1.469 | 10.71% | 0.85 | PS 315 | 1.469 | 10.71%
[34 empty] | 0.86 | PS 315 | 1.469 | 14.29% | 0.86 | PS 315 | 1.469 | 14.29% | 0.86 | PS 315 | 1.469 | 14.29%
[34 empty] | 0.87 | PS 315 | 1.469 | 17.86% | 0.87 | PS 315 | 1.469 | 17.86% | 0.87 | PS 315 | 1.469 | 17.86%
[34 empty] | 0.88 | PS 315 | 1.469 | 21.43% | 0.88 | PS 315 | 1.469 | 21.43% | 0.88 | PS 315 | 1.469 | 21.43%
[34 empty] | 0.89 | PS 315 | 1.469 | 25% | 0.89 | PS 315 | 1.469 | 25% | 0.89 | PS 315 | 1.469 | 25%
[34 empty] | 0.9 | PS 315 | 1.469 | 28.57% | 0.9 | PS 315 | 1.469 | 28.57% | 0.9 | PS 315 | 1.469 | 28.57%
[34 empty] | 0.91 | PS 315 | 1.469 | 32.14% | 0.91 | PS 315 | 1.469 | 32.14% | 0.91 | PS 315 | 1.469 | 32.14%
[34 empty] | 0.92 | PS 315 | 1.469 | 35.71% | 0.92 | PS 315 | 1.469 | 35.71% | 0.92 | PS 315 | 1.469 | 35.71%
[34 empty] | 0.93 | PS 315 | 1.469 | 39.29% | 0.93 | PS 315 | 1.469 | 39.29% | 0.93 | PS 315 | 1.469 | 39.29%
[34 empty] | 0.94 | PS 315 | 1.469 | 42.86% | 0.94 | PS 315 | 1.469 | 42.86% | 0.94 | PS 315 | 1.469 | 42.86%
[34 empty] | 0.95 | PS 325 | 3.11 | 5% | 0.95 | PS 315 | 1.469 | 46.43% | 0.95 | PS 315 | 1.469 | 46.43%
[34 empty] | 0.96 | PS 325 | 3.11 | 10% | 0.96 | PS 315 | 1.469 | 50% | 0.96 | PS 315 | 1.469 | 50%
[34 empty] | 0.97 | PS 325 | 3.11 | 15% | 0.97 | PS 315 | 1.469 | 53.57% | 0.97 | PS 315 | 1.469 | 53.57%
[34 empty] | 0.98 | PS 325 | 3.11 | 20% | 0.98 | PS 315 | 1.469 | 57.14% | 0.98 | PS 315 | 1.469 | 57.14%
[34 empty] | 0.99 | PS 325 | 3.11 | 25% | 0.99 | PS 315 | 1.469 | 60.71% | 0.99 | PS 315 | 1.469 | 60.71%
[34 empty] | 1 | PS 325 | 3.11 | 30% | 1 | PS 315 | 1.469 | 64.29% | 1 | PS 315 | 1.469 | 64.29%
[34 empty] | 1.01 | PS 325 | 3.11 | 35% | 1.01 | PS 315 | 1.469 | 67.86% | 1.01 | PS 315 | 1.469 | 67.86%
[34 empty] | 1.02 | PS 325 | 3.11 | 40% | 1.02 | PS 315 | 1.469 | 71.43% | 1.02 | PS 315 | 1.469 | 71.43%
[34 empty] | 1.03 | PS 325 | 3.11 | 45% | 1.03 | PS 315 | 1.469 | 75% | 1.03 | PS 315 | 1.469 | 75%
[34 empty] | 1.04 | PS 325 | 3.11 | 50% | 1.04 | PS 315 | 1.469 | 78.57% | 1.04 | PS 315 | 1.469 | 78.57%
[34 empty] | 1.05 | PS 325 | 3.11 | 55% | 1.05 | PS 315 | 1.469 | 82.14% | 1.05 | PS 315 | 1.469 | 82.14%
[34 empty] | 1.06 | PS 340 | 1.57 | 3.571% | 1.06 | PS 340 | 1.57 | 3.571% | 1.06 | PS 340 | 1.57 | 3.571%
[34 empty] | 1.07 | PS 340 | 1.57 | 7.143% | 1.07 | PS 340 | 1.57 | 7.143% | 1.07 | PS 340 | 1.57 | 7.143%
[34 empty] | 1.08 | PS 340 | 1.57 | 10.71% | 1.08 | PS 340 | 1.57 | 10.71% | 1.08 | PS 340 | 1.57 | 10.71%
[34 empty] | 1.09 | PS 340 | 1.57 | 14.29% | 1.09 | PS 340 | 1.57 | 14.29% | 1.09 | PS 340 | 1.57 | 14.29%
[34 empty] | 1.1 | PS 340 | 1.57 | 17.86% | 1.1 | PS 340 | 1.57 | 17.86% | 1.1 | PS 340 | 1.57 | 17.86%
[34 empty] | 1.11 | PS 340 | 1.57 | 21.43% | 1.11 | PS 340 | 1.57 | 21.43% | 1.11 | PS 340 | 1.57 | 21.43%
[34 empty] | 1.12 | PS 340 | 1.57 | 25% | 1.12 | PS 340 | 1.57 | 25% | 1.12 | PS 340 | 1.57 | 25%
[34 empty] | 1.13 | PS 340 | 1.57 | 28.57% | 1.13 | PS 340 | 1.57 | 28.57% | 1.13 | PS 340 | 1.57 | 28.57%
[34 empty] | 1.14 | PS 425 | 3.622 | 3.333% | 1.14 | PS 340 | 1.57 | 32.14% | 1.14 | PS 340 | 1.57 | 32.14%
[34 empty] | 1.15 | PS 425 | 3.622 | 6.667% | 1.15 | PS 340 | 1.57 | 35.71% | 1.15 | PS 340 | 1.57 | 35.71%
[34 empty] | 1.16 | PS 425 | 3.622 | 10% | 1.16 | PS 340 | 1.57 | 39.29% | 1.16 | PS 340 | 1.57 | 39.29%
[34 empty] | 1.17 | PS 425 | 3.622 | 13.33% | 1.17 | PS 340 | 1.57 | 42.86% | 1.17 | PS 340 | 1.57 | 42.86%
[34 empty] | 1.18 | PS 425 | 3.622 | 16.67% | 1.18 | PS 340 | 1.57 | 46.43% | 1.18 | PS 340 | 1.57 | 46.43%
[34 empty] | 1.19 | PS 425 | 3.622 | 20% | 1.19 | PS 340 | 1.57 | 50% | 1.19 | PS 340 | 1.57 | 50%
[34 empty] | 1.2 | PS 425 | 3.622 | 23.33% | 1.2 | PS 340 | 1.57 | 53.57% | 1.2 | PS 340 | 1.57 | 53.57%
[34 empty] | 1.21 | PS 425 | 3.622 | 26.67% | 1.21 | PS 340 | 1.57 | 57.14% | 1.21 | PS 340 | 1.57 | 57.14%
[34 empty] | 1.22 | PS 425 | 3.622 | 30% | 1.22 | PS 340 | 1.57 | 60.71% | 1.22 | PS 340 | 1.57 | 60.71%
[34 empty] | 1.23 | PS 425 | 3.622 | 33.33% | 1.23 | PS 340 | 1.57 | 64.29% | 1.23 | PS 340 | 1.57 | 64.29%
[34 empty] | 1.24 | PS 425 | 3.622 | 36.67% | 1.24 | PS 340 | 1.57 | 67.86% | 1.24 | PS 340 | 1.57 | 67.86%
[34 empty] | 1.25 | PS 425 | 3.622 | 40% | 1.25 | PS 340 | 1.57 | 71.43% | 1.25 | PS 340 | 1.57 | 71.43%
[34 empty] | 1.26 | PS 425 | 3.622 | 43.33% | 1.26 | PS 340 | 1.57 | 75% | 1.26 | PS 340 | 1.57 | 75%
[34 empty] | 1.27 | PS 425 | 3.622 | 46.67% | 1.27 | PS 340 | 1.57 | 78.57% | 1.27 | PS 340 | 1.57 | 78.57%
[34 empty] | 1.28 | PS 425 | 3.622 | 50% | 1.28 | PS 340 | 1.57 | 82.14% | 1.28 | PS 340 | 1.57 | 82.14%
[34 empty] | 1.29 | PS 425 | 3.622 | 53.33% | 1.29 | PS 360 | 2.106 | 0% | 1.29 | PS 360 | 2.106 | 0%
[34 empty] | 1.3 | PS 360 | 2.106 | 2.778% | 1.3 | PS 360 | 2.106 | 2.778% | 1.3 | PS 360 | 2.106 | 2.778%
[34 empty] | 1.31 | PS 360 | 2.106 | 5.556% | 1.31 | PS 360 | 2.106 | 5.556% | 1.31 | PS 360 | 2.106 | 5.556%
[34 empty] | 1.32 | PS 360 | 2.106 | 8.333% | 1.32 | PS 360 | 2.106 | 8.333% | 1.32 | PS 360 | 2.106 | 8.333%
[34 empty] | 1.33 | PS 360 | 2.106 | 11.11% | 1.33 | PS 360 | 2.106 | 11.11% | 1.33 | PS 360 | 2.106 | 11.11%
[34 empty] | 1.34 | PS 360 | 2.106 | 13.89% | 1.34 | PS 360 | 2.106 | 13.89% | 1.34 | PS 360 | 2.106 | 13.89%
[34 empty] | 1.35 | PS 360 | 2.106 | 16.67% | 1.35 | PS 360 | 2.106 | 16.67% | 1.35 | PS 360 | 2.106 | 16.67%
[34 empty] | 1.36 | PS 360 | 2.106 | 19.44% | 1.36 | PS 360 | 2.106 | 19.44% | 1.36 | PS 360 | 2.106 | 19.44%
[34 empty] | 1.37 | PS 360 | 2.106 | 22.22% | 1.37 | PS 360 | 2.106 | 22.22% | 1.37 | PS 360 | 2.106 | 22.22%
[34 empty] | 1.38 | PS 360 | 2.106 | 25% | 1.38 | PS 360 | 2.106 | 25% | 1.38 | PS 360 | 2.106 | 25%
[34 empty] | 1.39 | PS 360 | 2.106 | 27.78% | 1.39 | PS 360 | 2.106 | 27.78% | 1.39 | PS 360 | 2.106 | 27.78%
[34 empty] | 1.4 | PS 360 | 2.106 | 30.56% | 1.4 | PS 360 | 2.106 | 30.56% | 1.4 | PS 360 | 2.106 | 30.56%
[34 empty] | 1.41 | PS 360 | 2.106 | 33.33% | 1.41 | PS 360 | 2.106 | 33.33% | 1.41 | PS 360 | 2.106 | 33.33%
[34 empty] | 1.42 | PS 360 | 2.106 | 36.11% | 1.42 | PS 360 | 2.106 | 36.11% | 1.42 | PS 360 | 2.106 | 36.11%
[34 empty] | 1.43 | PS 400 | 3.622 | 0% | 1.43 | PS 360 | 2.106 | 38.89% | 1.43 | PS 360 | 2.106 | 38.89%
[34 empty] | 1.44 | PS 400 | 3.622 | 2.273% | 1.44 | PS 360 | 2.106 | 41.67% | 1.44 | PS 360 | 2.106 | 41.67%
[34 empty] | 1.45 | PS 400 | 3.622 | 4.545% | 1.45 | PS 360 | 2.106 | 44.44% | 1.45 | PS 360 | 2.106 | 44.44%
[34 empty] | 1.46 | PS 400 | 3.622 | 6.818% | 1.46 | PS 360 | 2.106 | 47.22% | 1.46 | PS 360 | 2.106 | 47.22%
[34 empty] | 1.47 | PS 400 | 3.622 | 9.091% | 1.47 | PS 360 | 2.106 | 50% | 1.47 | PS 360 | 2.106 | 50%
[34 empty] | 1.48 | PS 400 | 3.622 | 11.36% | 1.48 | PS 360 | 2.106 | 52.78% | 1.48 | PS 360 | 2.106 | 52.78%
[34 empty] | 1.49 | PS 400 | 3.622 | 13.64% | 1.49 | PS 410 | 2.598 | 2.326% | 1.49 | PS 360 | 2.106 | 55.56%
[34 empty] | 1.5 | PS 400 | 3.622 | 15.91% | 1.5 | PS 410 | 2.598 | 4.651% | 1.5 | PS 360 | 2.106 | 58.33%
[34 empty] | 1.51 | PS 400 | 3.622 | 18.18% | 1.51 | PS 410 | 2.598 | 6.977% | 1.51 | PS 360 | 2.106 | 61.11%
[34 empty] | 1.52 | PS 400 | 3.622 | 20.45% | 1.52 | PS 410 | 2.598 | 9.302% | 1.52 | PS 360 | 2.106 | 63.89%
[34 empty] | 1.53 | PS 400 | 3.622 | 22.73% | 1.53 | PS 410 | 2.598 | 11.63% | 1.53 | PS 360 | 2.106 | 66.67%
[34 empty] | 1.54 | PS 410 | 2.598 | 13.95% | 1.54 | PS 360 | 2.106 | 69.44% | 1.54 | PS 360 | 2.106 | 69.44%
[34 empty] | 1.55 | PS 410 | 2.598 | 16.28% | 1.55 | PS 360 | 2.106 | 72.22% | 1.55 | PS 360 | 2.106 | 72.22%
[34 empty] | 1.56 | PS 410 | 2.598 | 18.6% | 1.56 | PS 360 | 2.106 | 75% | 1.56 | PS 360 | 2.106 | 75%
[34 empty] | 1.57 | PS 410 | 2.598 | 20.93% | 1.57 | PS 360 | 2.106 | 77.78% | 1.57 | PS 360 | 2.106 | 77.78%
[34 empty] | 1.58 | PS 410 | 2.598 | 23.26% | 1.58 | PS 360 | 2.106 | 80.56% | 1.58 | PS 360 | 2.106 | 80.56%
[34 empty] | 1.59 | PS 410 | 2.598 | 25.58% | 1.59 | PS 360 | 2.106 | 83.33% | 1.59 | PS 360 | 2.106 | 83.33%
[34 empty] | 1.6 | PS 410 | 2.598 | 27.91% | 1.6 | PS 360 | 2.106 | 86.11% | 1.6 | PS 360 | 2.106 | 86.11%
[34 empty] | 1.61 | PS 410 | 2.598 | 30.23% | 1.61 | PS 360 | 2.106 | 88.89% | 1.61 | PS 360 | 2.106 | 88.89%
[34 empty] | 1.62 | PS 410 | 2.598 | 32.56% | 1.62 | PS 360 | 2.106 | 91.67% | 1.62 | PS 360 | 2.106 | 91.67%
[34 empty] | 1.63 | PS 475 | 2.63 | 2.174% | 1.63 | PS 410 | 2.598 | 34.88% | 1.63 | PS 360 | 2.106 | 94.44%
[34 empty] | 1.64 | PS 475 | 2.63 | 4.348% | 1.64 | PS 410 | 2.598 | 37.21% | 1.64 | PS 360 | 2.106 | 97.22%
[34 empty] | 1.65 | PS 475 | 2.63 | 6.522% | 1.65 | PS 410 | 2.598 | 39.53% | 1.65 | PS 410 | 2.598 | 39.53%
[34 empty] | 1.66 | PS 475 | 2.63 | 8.696% | 1.66 | PS 410 | 2.598 | 41.86% | 1.66 | PS 410 | 2.598 | 41.86%
[34 empty] | 1.67 | PS 475 | 2.63 | 10.87% | 1.67 | PS 410 | 2.598 | 44.19% | 1.67 | PS 410 | 2.598 | 44.19%
[34 empty] | 1.68 | PS 475 | 2.63 | 13.04% | 1.68 | PS 410 | 2.598 | 46.51% | 1.68 | PS 410 | 2.598 | 46.51%
[34 empty] | 1.69 | PS 475 | 2.63 | 15.22% | 1.69 | PS 410 | 2.598 | 48.84% | 1.69 | PS 410 | 2.598 | 48.84%
[34 empty] | 1.7 | PS 475 | 2.63 | 17.39% | 1.7 | PS 410 | 2.598 | 51.16% | 1.7 | PS 410 | 2.598 | 51.16%
[34 empty] | 1.71 | PS 475 | 2.63 | 19.57% | 1.71 | PS 410 | 2.598 | 53.49% | 1.71 | PS 410 | 2.598 | 53.49%
[34 empty] | 1.72 | PS 475 | 2.63 | 21.74% | 1.72 | PS 410 | 2.598 | 55.81% | 1.72 | PS 410 | 2.598 | 55.81%
[34 empty] | 1.73 | PS 475 | 2.63 | 23.91% | 1.73 | PS 410 | 2.598 | 58.14% | 1.73 | PS 410 | 2.598 | 58.14%
[34 empty] | 1.74 | PS 475 | 2.63 | 26.09% | 1.74 | PS 410 | 2.598 | 60.47% | 1.74 | PS 410 | 2.598 | 60.47%
[34 empty] | 1.75 | PS 475 | 2.63 | 28.26% | 1.75 | PS 410 | 2.598 | 62.79% | 1.75 | PS 410 | 2.598 | 62.79%
[34 empty] | 1.76 | PS 475 | 2.63 | 30.43% | 1.76 | PS 410 | 2.598 | 65.12% | 1.76 | PS 410 | 2.598 | 65.12%
[34 empty] | 1.77 | PS 475 | 2.63 | 32.61% | 1.77 | PS 410 | 2.598 | 67.44% | 1.77 | PS 410 | 2.598 | 67.44%
[34 empty] | 1.78 | PS 475 | 2.63 | 34.78% | 1.78 | PS 410 | 2.598 | 69.77% | 1.78 | PS 410 | 2.598 | 69.77%
[34 empty] | 1.79 | PS 475 | 2.63 | 36.96% | 1.79 | PS 410 | 2.598 | 72.09% | 1.79 | PS 410 | 2.598 | 72.09%
[34 empty] | 1.8 | PS 475 | 2.63 | 39.13% | 1.8 | PS 410 | 2.598 | 74.42% | 1.8 | PS 410 | 2.598 | 74.42%
[34 empty] | 1.81 | PS 475 | 2.63 | 41.3% | 1.81 | PS 410 | 2.598 | 76.74% | 1.81 | PS 410 | 2.598 | 76.74%
[34 empty] | 1.82 | PS 475 | 2.63 | 43.48% | 1.82 | PS 410 | 2.598 | 79.07% | 1.82 | PS 410 | 2.598 | 79.07%
[34 empty] | 1.83 | PS 475 | 2.63 | 45.65% | 1.83 | PS 410 | 2.598 | 81.4% | 1.83 | PS 410 | 2.598 | 81.4%
[34 empty] | 1.84 | PS 475 | 2.63 | 47.83% | 1.84 | PS 410 | 2.598 | 83.72% | 1.84 | PS 410 | 2.598 | 83.72%
[34 empty] | 1.85 | PS 475 | 2.63 | 50% | 1.85 | PS 410 | 2.598 | 86.05% | 1.85 | PS 410 | 2.598 | 86.05%
[34 empty] | 1.86 | PS 475 | 2.63 | 52.17% | 1.86 | PS 410 | 2.598 | 88.37% | 1.86 | PS 410 | 2.598 | 88.37%
[34 empty] | 1.87 | PS 475 | 2.63 | 54.35% | 1.87 | PS 475 | 2.63 | 54.35% | 1.87 | PS 410 | 2.598 | 90.7%
[34 empty] | 1.88 | PS 475 | 2.63 | 56.52% | 1.88 | PS 475 | 2.63 | 56.52% | 1.88 | PS 410 | 2.598 | 93.02%
[34 empty] | 1.89 | PS 575 | 3.1 | 2.128% | 1.89 | PS 475 | 2.63 | 58.7% | 1.89 | PS 410 | 2.598 | 95.35%
[34 empty] | 1.9 | PS 575 | 3.1 | 4.255% | 1.9 | PS 475 | 2.63 | 60.87% | 1.9 | PS 475 | 2.63 | 60.87%
[34 empty] | 1.91 | PS 575 | 3.1 | 6.383% | 1.91 | PS 475 | 2.63 | 63.04% | 1.91 | PS 475 | 2.63 | 63.04%
[34 empty] | 1.92 | PS 575 | 3.1 | 8.511% | 1.92 | PS 475 | 2.63 | 65.22% | 1.92 | PS 475 | 2.63 | 65.22%
[34 empty] | 1.93 | PS 575 | 3.1 | 10.64% | 1.93 | PS 475 | 2.63 | 67.39% | 1.93 | PS 475 | 2.63 | 67.39%
[34 empty] | 1.94 | PS 575 | 3.1 | 12.77% | 1.94 | PS 475 | 2.63 | 69.57% | 1.94 | PS 475 | 2.63 | 69.57%
[34 empty] | 1.95 | PS 575 | 3.1 | 14.89% | 1.95 | PS 475 | 2.63 | 71.74% | 1.95 | PS 475 | 2.63 | 71.74%
[34 empty] | 1.96 | PS 575 | 3.1 | 17.02% | 1.96 | PS 475 | 2.63 | 73.91% | 1.96 | PS 475 | 2.63 | 73.91%
[34 empty] | 1.97 | PS 575 | 3.1 | 19.15% | 1.97 | PS 475 | 2.63 | 76.09% | 1.97 | PS 475 | 2.63 | 76.09%
[34 empty] | 1.98 | PS 575 | 3.1 | 21.28% | 1.98 | PS 475 | 2.63 | 78.26% | 1.98 | PS 475 | 2.63 | 78.26%
[34 empty] | 1.99 | PS 575 | 3.1 | 23.4% | 1.99 | PS 475 | 2.63 | 80.43% | 1.99 | PS 475 | 2.63 | 80.43%
[34 empty] | 2 | PS 575 | 3.1 | 25.53% | 2 | PS 475 | 2.63 | 82.61% | 2 | PS 475 | 2.63 | 82.61%
[34 empty] | 2.01 | PS 575 | 3.1 | 27.66% | 2.01 | PS 475 | 2.63 | 84.78% | 2.01 | PS 475 | 2.63 | 84.78%
[34 empty] | 2.02 | PS 575 | 3.1 | 29.79% | 2.02 | PS 475 | 2.63 | 86.96% | 2.02 | PS 475 | 2.63 | 86.96%
[34 empty] | 2.03 | PS 575 | 3.1 | 31.91% | 2.03 | PS 475 | 2.63 | 89.13% | 2.03 | PS 475 | 2.63 | 89.13%
[34 empty] | 2.04 | PS 575 | 3.1 | 34.04% | 2.04 | PS 475 | 2.63 | 91.3% | 2.04 | PS 475 | 2.63 | 91.3%
[34 empty] | 2.05 | PS 575 | 3.1 | 36.17% | 2.05 | PS 475 | 2.63 | 93.48% | 2.05 | PS 475 | 2.63 | 93.48%
[34 empty] | 2.06 | PS 575 | 3.1 | 38.3% | 2.06 | PS 575 | 3.1 | 38.3% | 2.06 | PS 575 | 3.1 | 38.3%
[34 empty] | 2.07 | PS 575 | 3.1 | 40.43% | 2.07 | PS 575 | 3.1 | 40.43% | 2.07 | PS 575 | 3.1 | 40.43%
[34 empty] | 2.08 | PS 575 | 3.1 | 42.55% | 2.08 | PS 575 | 3.1 | 42.55% | 2.08 | PS 575 | 3.1 | 42.55%
[34 empty] | 2.09 | PS 575 | 3.1 | 44.68% | 2.09 | PS 575 | 3.1 | 44.68% | 2.09 | PS 575 | 3.1 | 44.68%
[34 empty] | 2.1 | PS 575 | 3.1 | 46.81% | 2.1 | PS 575 | 3.1 | 46.81% | 2.1 | PS 575 | 3.1 | 46.81%
[34 empty] | 2.11 | PS 575 | 3.1 | 48.94% | 2.11 | PS 575 | 3.1 | 48.94% | 2.11 | PS 575 | 3.1 | 48.94%
[34 empty] | 2.12 | PS 575 | 3.1 | 51.06% | 2.12 | PS 575 | 3.1 | 51.06% | 2.12 | PS 575 | 3.1 | 51.06%
[34 empty] | 2.13 | PS 575 | 3.1 | 53.19% | 2.13 | PS 575 | 3.1 | 53.19% | 2.13 | PS 575 | 3.1 | 53.19%
[34 empty] | 2.14 | PS 575 | 3.1 | 55.32% | 2.14 | PS 575 | 3.1 | 55.32% | 2.14 | PS 575 | 3.1 | 55.32%
[34 empty] | 2.15 | PS 575 | 3.1 | 57.45% | 2.15 | PS 575 | 3.1 | 57.45% | 2.15 | PS 575 | 3.1 | 57.45%
[34 empty] | 2.16 | PS 575 | 3.1 | 59.57% | 2.16 | PS 575 | 3.1 | 59.57% | 2.16 | PS 575 | 3.1 | 59.57%
[34 empty] | 2.17 | PS 575 | 3.1 | 61.7% | 2.17 | PS 575 | 3.1 | 61.7% | 2.17 | PS 575 | 3.1 | 61.7%
[34 empty] | 2.18 | PS 575 | 3.1 | 63.83% | 2.18 | PS 575 | 3.1 | 63.83% | 2.18 | PS 575 | 3.1 | 63.83%
[34 empty] | 2.19 | PS 525 | 3.86 | 2.5% | 2.19 | PS 575 | 3.1 | 65.96% | 2.19 | PS 575 | 3.1 | 65.96%
[34 empty] | 2.2 | PS 525 | 3.86 | 5% | 2.2 | PS 575 | 3.1 | 68.09% | 2.2 | PS 575 | 3.1 | 68.09%
[34 empty] | 2.21 | PS 525 | 3.86 | 7.5% | 2.21 | PS 575 | 3.1 | 70.21% | 2.21 | PS 575 | 3.1 | 70.21%
[34 empty] | 2.22 | PS 525 | 3.86 | 10% | 2.22 | PS 575 | 3.1 | 72.34% | 2.22 | PS 575 | 3.1 | 72.34%
[34 empty] | 2.23 | PS 525 | 3.86 | 12.5% | 2.23 | PS 575 | 3.1 | 74.47% | 2.23 | PS 575 | 3.1 | 74.47%
[34 empty] | 2.24 | PS 525 | 3.86 | 15% | 2.24 | PS 575 | 3.1 | 76.6% | 2.24 | PS 575 | 3.1 | 76.6%
[34 empty] | 2.25 | PS 525 | 3.86 | 17.5% | 2.25 | PS 575 | 3.1 | 78.72% | 2.25 | PS 575 | 3.1 | 78.72%
[34 empty] | 2.26 | PS 525 | 3.86 | 20% | 2.26 | PS 575 | 3.1 | 80.85% | 2.26 | PS 575 | 3.1 | 80.85%
[34 empty] | 2.27 | PS 525 | 3.86 | 22.5% | 2.27 | PS 575 | 3.1 | 82.98% | 2.27 | PS 575 | 3.1 | 82.98%
[34 empty] | 2.28 | PS 525 | 3.86 | 25% | 2.28 | PS 575 | 3.1 | 85.11% | 2.28 | PS 575 | 3.1 | 85.11%
[34 empty] | 2.29 | PS 525 | 3.86 | 27.5% | 2.29 | PS 575 | 3.1 | 87.23% | 2.29 | PS 575 | 3.1 | 87.23%
[34 empty] | 2.3 | PS 525 | 3.86 | 30% | 2.3 | PS 575 | 3.1 | 89.36% | 2.3 | PS 575 | 3.1 | 89.36%
[34 empty] | 2.31 | PS 525 | 3.86 | 32.5% | 2.31 | PS 575 | 3.1 | 91.49% | 2.31 | PS 575 | 3.1 | 91.49%
[34 empty] | 2.32 | PS 525 | 3.86 | 35% | 2.32 | PS 575 | 3.1 | 93.62% | 2.32 | PS 575 | 3.1 | 93.62%
[34 empty] | 2.33 | PS 525 | 3.86 | 37.5% | 2.33 | PS 575 | 3.1 | 95.74% | 2.33 | PS 575 | 3.1 | 95.74%
[34 empty] | 2.34 | PS 525 | 3.86 | 40% | 2.34 | PS 525 | 3.86 | 40% | 2.34 | PS 525 | 3.86 | 40%
[34 empty] | 2.35 | PS 525 | 3.86 | 42.5% | 2.35 | PS 525 | 3.86 | 42.5% | 2.35 | PS 525 | 3.86 | 42.5%
[34 empty] | 2.36 | PS 525 | 3.86 | 45% | 2.36 | PS 525 | 3.86 | 45% | 2.36 | PS 525 | 3.86 | 45%
[34 empty] | 2.37 | PS 525 | 3.86 | 47.5% | 2.37 | PS 525 | 3.86 | 47.5% | 2.37 | PS 525 | 3.86 | 47.5%
[34 empty] | 2.38 | PS 500 | 3.86 | 2.273% | 2.38 | PS 500 | 3.86 | 2.273% | 2.38 | PS 500 | 3.86 | 2.273%
[34 empty] | 2.39 | PS 500 | 3.86 | 4.545% | 2.39 | PS 500 | 3.86 | 4.545% | 2.39 | PS 500 | 3.86 | 4.545%
[34 empty] | 2.4 | PS 500 | 3.86 | 6.818% | 2.4 | PS 500 | 3.86 | 6.818% | 2.4 | PS 500 | 3.86 | 6.818%
[34 empty] | 2.41 | PS 500 | 3.86 | 9.091% | 2.41 | PS 500 | 3.86 | 9.091% | 2.41 | PS 500 | 3.86 | 9.091%
[34 empty] | 2.42 | PS 500 | 3.86 | 11.36% | 2.42 | PS 500 | 3.86 | 11.36% | 2.42 | PS 500 | 3.86 | 11.36%
[34 empty] | 2.43 | PS 500 | 3.86 | 13.64% | 2.43 | PS 500 | 3.86 | 13.64% | 2.43 | PS 500 | 3.86 | 13.64%
[34 empty] | 2.44 | PS 500 | 3.86 | 15.91% | 2.44 | PS 500 | 3.86 | 15.91% | 2.44 | PS 500 | 3.86 | 15.91%
[34 empty] | 2.45 | PS 500 | 3.86 | 18.18% | 2.45 | PS 500 | 3.86 | 18.18% | 2.45 | PS 500 | 3.86 | 18.18%
[34 empty] | 2.46 | PS 500 | 3.86 | 20.45% | 2.46 | PS 500 | 3.86 | 20.45% | 2.46 | PS 500 | 3.86 | 20.45%
[34 empty] | 2.47 | PS 500 | 3.86 | 22.73% | 2.47 | PS 500 | 3.86 | 22.73% | 2.47 | PS 500 | 3.86 | 22.73%
[34 empty] | 2.48 | PS 500 | 3.86 | 25% | 2.48 | PS 500 | 3.86 | 25% | 2.48 | PS 500 | 3.86 | 25%
[34 empty] | 2.49 | PS 500 | 3.86 | 27.27% | 2.49 | PS 500 | 3.86 | 27.27% | 2.49 | PS 500 | 3.86 | 27.27%
[34 empty] | 2.5 | PS 500 | 3.86 | 29.55% | 2.5 | PS 500 | 3.86 | 29.55% | 2.5 | PS 500 | 3.86 | 29.55%
[34 empty] | 2.51 | PS 500 | 3.86 | 31.82% | 2.51 | PS 500 | 3.86 | 31.82% | 2.51 | PS 500 | 3.86 | 31.82%
[34 empty] | 2.52 | PS 500 | 3.86 | 34.09% | 2.52 | PS 500 | 3.86 | 34.09% | 2.52 | PS 500 | 3.86 | 34.09%
[34 empty] | 2.53 | PS 500 | 3.86 | 36.36% | 2.53 | PS 500 | 3.86 | 36.36% | 2.53 | PS 500 | 3.86 | 36.36%
[34 empty] | 2.54 | PS 500 | 3.86 | 38.64% | 2.54 | PS 500 | 3.86 | 38.64% | 2.54 | PS 500 | 3.86 | 38.64%
[34 empty] | 2.55 | PS 500 | 3.86 | 40.91% | 2.55 | PS 500 | 3.86 | 40.91% | 2.55 | PS 500 | 3.86 | 40.91%
[34 empty] | 2.56 | PS 500 | 3.86 | 43.18% | 2.56 | PS 500 | 3.86 | 43.18% | 2.56 | PS 500 | 3.86 | 43.18%
[34 empty] | 2.57 | PS 500 | 3.86 | 45.45% | 2.57 | PS 500 | 3.86 | 45.45% | 2.57 | PS 500 | 3.86 | 45.45%
[34 empty] | 2.58 | PS 500 | 3.86 | 47.73% | 2.58 | PS 500 | 3.86 | 47.73% | 2.58 | PS 500 | 3.86 | 47.73%
[34 empty] | 2.59 | PS 500 | 3.86 | 50% | 2.59 | PS 500 | 3.86 | 50% | 2.59 | PS 500 | 3.86 | 50%
[34 empty] | 2.6 | PS 500 | 3.86 | 52.27% | 2.6 | PS 500 | 3.86 | 52.27% | 2.6 | PS 500 | 3.86 | 52.27%
[34 empty] | 2.61 | PS 500 | 3.86 | 54.55% | 2.61 | PS 500 | 3.86 | 54.55% | 2.61 | PS 500 | 3.86 | 54.55%
[34 empty] | 2.62 | PS 500 | 3.86 | 56.82% | 2.62 | PS 500 | 3.86 | 56.82% | 2.62 | PS 500 | 3.86 | 56.82%
[34 empty] | 2.63 | PS 500 | 3.86 | 59.09% | 2.63 | PS 500 | 3.86 | 59.09% | 2.63 | PS 500 | 3.86 | 59.09%
[34 empty] | 2.64 | PS 500 | 3.86 | 61.36% | 2.64 | PS 500 | 3.86 | 61.36% | 2.64 | PS 500 | 3.86 | 61.36%
[34 empty] | 2.65 | PS 500 | 3.86 | 63.64% | 2.65 | PS 500 | 3.86 | 63.64% | 2.65 | PS 500 | 3.86 | 63.64%
[34 empty] | 2.66 | PS 500 | 3.86 | 65.91% | 2.66 | PS 500 | 3.86 | 65.91% | 2.66 | PS 500 | 3.86 | 65.91%
[34 empty] | 2.67 | PS 500 | 3.86 | 68.18% | 2.67 | PS 500 | 3.86 | 68.18% | 2.67 | PS 500 | 3.86 | 68.18%
[34 empty] | 2.68 | PS 500 | 3.86 | 70.45% | 2.68 | PS 500 | 3.86 | 70.45% | 2.68 | PS 500 | 3.86 | 70.45%
[34 empty] | 2.69 | PS 500 | 3.86 | 72.73% | 2.69 | PS 500 | 3.86 | 72.73% | 2.69 | PS 500 | 3.86 | 72.73%
[34 empty] | 2.7 | PS 500 | 3.86 | 75% | 2.7 | PS 500 | 3.86 | 75% | 2.7 | PS 500 | 3.86 | 75%
[34 empty] | 2.71 | PS 500 | 3.86 | 77.27% | 2.71 | PS 500 | 3.86 | 77.27% | 2.71 | PS 500 | 3.86 | 77.27%
[34 empty] | 2.72 | PS 500 | 3.86 | 79.55% | 2.72 | PS 500 | 3.86 | 79.55% | 2.72 | PS 500 | 3.86 | 79.55%
[34 empty] | 2.73 | PS 500 | 3.86 | 81.82% | 2.73 | PS 500 | 3.86 | 81.82% | 2.73 | PS 500 | 3.86 | 81.82%
[34 empty] | 2.74 | PS 500 | 3.86 | 84.09% | 2.74 | PS 500 | 3.86 | 84.09% | 2.74 | PS 500 | 3.86 | 84.09%
[34 empty] | 2.75 | PS 500 | 3.86 | 86.36% | 2.75 | PS 500 | 3.86 | 86.36% | 2.75 | PS 500 | 3.86 | 86.36%
[34 empty] | 2.76 | PS 500 | 3.86 | 88.64% | 2.76 | PS 500 | 3.86 | 88.64% | 2.76 | PS 500 | 3.86 | 88.64%
[34 empty] | 2.77 | PS 500 | 3.86 | 90.91% | 2.77 | PS 500 | 3.86 | 90.91% | 2.77 | PS 500 | 3.86 | 90.91%
[34 empty] | 2.78 | PS 500 | 3.86 | 93.18% | 2.78 | PS 500 | 3.86 | 93.18% | 2.78 | PS 500 | 3.86 | 93.18%
[34 empty] | 2.79 | PS 500 | 3.86 | 95.45% | 2.79 | PS 500 | 3.86 | 95.45% | 2.79 | PS 500 | 3.86 | 95.45%
[34 empty] | 2.8 | PS 500 | 3.86 | 97.73% | 2.8 | PS 500 | 3.86 | 97.73% | 2.8 | PS 500 | 3.86 | 97.73%
[34 empty] | 2.81 | PS 500 | 3.86 | 100% | 2.81 | PS 500 | 3.86 | 100% | 2.81 | PS 500 | 3.86 | 100%
[34 empty] | 2.82 | N/A | N/A | N/A | 2.82 | N/A | N/A | N/A | 2.82 | N/A | N/A | N/A
[34 empty] | 2.83 | N/A | N/A | N/A | 2.83 | N/A | N/A | N/A | 2.83 | N/A | N/A | N/A
[34 empty] | 2.84 | N/A | N/A | N/A | 2.84 | N/A | N/A | N/A | 2.84 | N/A | N/A | N/A
[34 empty] | 2.85 | N/A | N/A | N/A | 2.85 | N/A | N/A | N/A | 2.85 | N/A | N/A | N/A
[34 empty] | 2.86 | N/A | N/A | N/A | 2.86 | N/A | N/A | N/A | 2.86 | N/A | N/A | N/A
[34 empty] | 2.87 | N/A | N/A | N/A | 2.87 | N/A | N/A | N/A | 2.87 | N/A | N/A | N/A
[34 empty] | 2.88 | N/A | N/A | N/A | 2.88 | N/A | N/A | N/A | 2.88 | N/A | N/A | N/A
[34 empty] | 2.89 | N/A | N/A | N/A | 2.89 | N/A | N/A | N/A | 2.89 | N/A | N/A | N/A
[34 empty] | 2.9 | N/A | N/A | N/A | 2.9 | N/A | N/A | N/A | 2.9 | N/A | N/A | N/A
[34 empty] | 2.91 | N/A | N/A | N/A | 2.91 | N/A | N/A | N/A | 2.91 | N/A | N/A | N/A
[34 empty] | 2.92 | N/A | N/A | N/A | 2.92 | N/A | N/A | N/A | 2.92 | N/A | N/A | N/A
[34 empty] | 2.93 | N/A | N/A | N/A | 2.93 | N/A | N/A | N/A | 2.93 | N/A | N/A | N/A
[34 empty] | 2.94 | N/A | N/A | N/A | 2.94 | N/A | N/A | N/A | 2.94 | N/A | N/A | N/A
[34 empty] | 2.95 | N/A | N/A | N/A | 2.95 | N/A | N/A | N/A | 2.95 | N/A | N/A | N/A
[34 empty] | 2.96 | N/A | N/A | N/A | 2.96 | N/A | N/A | N/A | 2.96 | N/A | N/A | N/A
[34 empty] | 2.97 | N/A | N/A | N/A | 2.97 | N/A | N/A | N/A | 2.97 | N/A | N/A | N/A
[34 empty] | 2.98 | N/A | N/A | N/A | 2.98 | N/A | N/A | N/A | 2.98 | N/A | N/A | N/A
[34 empty] | 2.99 | N/A | N/A | N/A | 2.99 | N/A | N/A | N/A | 2.99 | N/A | N/A | N/A
[34 empty] | 3 | N/A | N/A | N/A | 3 | N/A | N/A | N/A | 3 | N/A | N/A | N/A
[34 empty] | 3.01 | N/A | N/A | N/A | 3.01 | N/A | N/A | N/A | 3.01 | N/A | N/A | N/A
[34 empty] | 3.02 | N/A | N/A | N/A | 3.02 | N/A | N/A | N/A | 3.02 | N/A | N/A | N/A
[34 empty] | 3.03 | N/A | N/A | N/A | 3.03 | N/A | N/A | N/A | 3.03 | N/A | N/A | N/A
[34 empty] | 3.04 | N/A | N/A | N/A | 3.04 | N/A | N/A | N/A | 3.04 | N/A | N/A | N/A
[34 empty] | 3.05 | N/A | N/A | N/A | 3.05 | N/A | N/A | N/A | 3.05 | N/A | N/A | N/A
[34 empty] | 3.06 | N/A | N/A | N/A | 3.06 | N/A | N/A | N/A | 3.06 | N/A | N/A | N/A
[34 empty] | 3.07 | N/A | N/A | N/A | 3.07 | N/A | N/A | N/A | 3.07 | N/A | N/A | N/A
[34 empty] | 3.08 | N/A | N/A | N/A | 3.08 | N/A | N/A | N/A | 3.08 | N/A | N/A | N/A
[34 empty] | 3.09 | N/A | N/A | N/A | 3.09 | N/A | N/A | N/A | 3.09 | N/A | N/A | N/A
[34 empty] | 3.1 | N/A | N/A | N/A | 3.1 | N/A | N/A | N/A | 3.1 | N/A | N/A | N/A
[34 empty] | 3.11 | N/A | N/A | N/A | 3.11 | N/A | N/A | N/A | 3.11 | N/A | N/A | N/A
[34 empty] | 3.12 | N/A | N/A | N/A | 3.12 | N/A | N/A | N/A | 3.12 | N/A | N/A | N/A
[34 empty] | 3.13 | N/A | N/A | N/A | 3.13 | N/A | N/A | N/A | 3.13 | N/A | N/A | N/A
[34 empty] | 3.14 | N/A | N/A | N/A | 3.14 | N/A | N/A | N/A | 3.14 | N/A | N/A | N/A
[34 empty] | 3.15 | N/A | N/A | N/A | 3.15 | N/A | N/A | N/A | 3.15 | N/A | N/A | N/A
[34 empty] | 3.16 | N/A | N/A | N/A | 3.16 | N/A | N/A | N/A | 3.16 | N/A | N/A | N/A
[34 empty] | 3.17 | N/A | N/A | N/A | 3.17 | N/A | N/A | N/A | 3.17 | N/A | N/A | N/A
[34 empty] | 3.18 | N/A | N/A | N/A | 3.18 | N/A | N/A | N/A | 3.18 | N/A | N/A | N/A
[34 empty] | 3.19 | N/A | N/A | N/A | 3.19 | N/A | N/A | N/A | 3.19 | N/A | N/A | N/A
[34 empty] | 3.2 | PS 600 | 6 | 0% | 3.2 | PS 600 | 6 | 0% | 3.2 | PS 600 | 6 | 0%
[34 empty] | 3.21 | PS 600 | 6 | 1.25% | 3.21 | PS 600 | 6 | 1.25% | 3.21 | PS 600 | 6 | 1.25%
[34 empty] | 3.22 | PS 600 | 6 | 2.5% | 3.22 | PS 600 | 6 | 2.5% | 3.22 | PS 600 | 6 | 2.5%
[34 empty] | 3.23 | PS 600 | 6 | 3.75% | 3.23 | PS 600 | 6 | 3.75% | 3.23 | PS 600 | 6 | 3.75%
[34 empty] | 3.24 | PS 600 | 6 | 5% | 3.24 | PS 600 | 6 | 5% | 3.24 | PS 600 | 6 | 5%
[34 empty] | 3.25 | PS 600 | 6 | 6.25% | 3.25 | PS 600 | 6 | 6.25% | 3.25 | PS 600 | 6 | 6.25%
[34 empty] | 3.26 | PS 600 | 6 | 7.5% | 3.26 | PS 600 | 6 | 7.5% | 3.26 | PS 600 | 6 | 7.5%
[34 empty] | 3.27 | PS 600 | 6 | 8.75% | 3.27 | PS 600 | 6 | 8.75% | 3.27 | PS 600 | 6 | 8.75%
[34 empty] | 3.28 | PS 600 | 6 | 10% | 3.28 | PS 600 | 6 | 10% | 3.28 | PS 600 | 6 | 10%
[34 empty] | 3.29 | PS 600 | 6 | 11.25% | 3.29 | PS 600 | 6 | 11.25% | 3.29 | PS 600 | 6 | 11.25%
[34 empty] | 3.3 | PS 600 | 6 | 12.5% | 3.3 | PS 600 | 6 | 12.5% | 3.3 | PS 600 | 6 | 12.5%
[34 empty] | 3.31 | PS 600 | 6 | 13.75% | 3.31 | PS 600 | 6 | 13.75% | 3.31 | PS 600 | 6 | 13.75%
[34 empty] | 3.32 | PS 600 | 6 | 15% | 3.32 | PS 600 | 6 | 15% | 3.32 | PS 600 | 6 | 15%
[34 empty] | 3.33 | PS 600 | 6 | 16.25% | 3.33 | PS 600 | 6 | 16.25% | 3.33 | PS 600 | 6 | 16.25%
[34 empty] | 3.34 | PS 600 | 6 | 17.5% | 3.34 | PS 600 | 6 | 17.5% | 3.34 | PS 600 | 6 | 17.5%
[34 empty] | 3.35 | PS 600 | 6 | 18.75% | 3.35 | PS 600 | 6 | 18.75% | 3.35 | PS 600 | 6 | 18.75%
[34 empty] | 3.36 | PS 600 | 6 | 20% | 3.36 | PS 600 | 6 | 20% | 3.36 | PS 600 | 6 | 20%
[34 empty] | 3.37 | PS 600 | 6 | 21.25% | 3.37 | PS 600 | 6 | 21.25% | 3.37 | PS 600 | 6 | 21.25%
[34 empty] | 3.38 | PS 600 | 6 | 22.5% | 3.38 | PS 600 | 6 | 22.5% | 3.38 | PS 600 | 6 | 22.5%
[34 empty] | 3.39 | PS 600 | 6 | 23.75% | 3.39 | PS 600 | 6 | 23.75% | 3.39 | PS 600 | 6 | 23.75%
[34 empty] | 3.4 | PS 600 | 6 | 25% | 3.4 | PS 600 | 6 | 25% | 3.4 | PS 600 | 6 | 25%
[34 empty] | 3.41 | PS 600 | 6 | 26.25% | 3.41 | PS 600 | 6 | 26.25% | 3.41 | PS 600 | 6 | 26.25%
[34 empty] | 3.42 | PS 600 | 6 | 27.5% | 3.42 | PS 600 | 6 | 27.5% | 3.42 | PS 600 | 6 | 27.5%
[34 empty] | 3.43 | PS 600 | 6 | 28.75% | 3.43 | PS 600 | 6 | 28.75% | 3.43 | PS 600 | 6 | 28.75%
[34 empty] | 3.44 | PS 600 | 6 | 30% | 3.44 | PS 600 | 6 | 30% | 3.44 | PS 600 | 6 | 30%
[34 empty] | 3.45 | PS 600 | 6 | 31.25% | 3.45 | PS 600 | 6 | 31.25% | 3.45 | PS 600 | 6 | 31.25%
[34 empty] | 3.46 | PS 600 | 6 | 32.5% | 3.46 | PS 600 | 6 | 32.5% | 3.46 | PS 600 | 6 | 32.5%
[34 empty] | 3.47 | PS 600 | 6 | 33.75% | 3.47 | PS 600 | 6 | 33.75% | 3.47 | PS 600 | 6 | 33.75%
[34 empty] | 3.48 | PS 600 | 6 | 35% | 3.48 | PS 600 | 6 | 35% | 3.48 | PS 600 | 6 | 35%
[34 empty] | 3.49 | PS 600 | 6 | 36.25% | 3.49 | PS 600 | 6 | 36.25% | 3.49 | PS 600 | 6 | 36.25%
[34 empty] | 3.5 | PS 600 | 6 | 37.5% | 3.5 | PS 600 | 6 | 37.5% | 3.5 | PS 600 | 6 | 37.5%
[34 empty] | 3.51 | PS 600 | 6 | 38.75% | 3.51 | PS 600 | 6 | 38.75% | 3.51 | PS 600 | 6 | 38.75%
[34 empty] | 3.52 | PS 600 | 6 | 40% | 3.52 | PS 600 | 6 | 40% | 3.52 | PS 600 | 6 | 40%
[34 empty] | 3.53 | PS 600 | 6 | 41.25% | 3.53 | PS 600 | 6 | 41.25% | 3.53 | PS 600 | 6 | 41.25%
[34 empty] | 3.54 | PS 600 | 6 | 42.5% | 3.54 | PS 600 | 6 | 42.5% | 3.54 | PS 600 | 6 | 42.5%
[34 empty] | 3.55 | PS 600 | 6 | 43.75% | 3.55 | PS 600 | 6 | 43.75% | 3.55 | PS 600 | 6 | 43.75%
[34 empty] | 3.56 | PS 600 | 6 | 45% | 3.56 | PS 600 | 6 | 45% | 3.56 | PS 600 | 6 | 45%
[34 empty] | 3.57 | PS 600 | 6 | 46.25% | 3.57 | PS 600 | 6 | 46.25% | 3.57 | PS 600 | 6 | 46.25%
[34 empty] | 3.58 | PS 600 | 6 | 47.5% | 3.58 | PS 600 | 6 | 47.5% | 3.58 | PS 600 | 6 | 47.5%
[34 empty] | 3.59 | PS 600 | 6 | 48.75% | 3.59 | PS 600 | 6 | 48.75% | 3.59 | PS 600 | 6 | 48.75%
[34 empty] | 3.6 | PS 600 | 6 | 50% | 3.6 | PS 600 | 6 | 50% | 3.6 | PS 600 | 6 | 50%
[34 empty] | 3.61 | PS 600 | 6 | 51.25% | 3.61 | PS 600 | 6 | 51.25% | 3.61 | PS 600 | 6 | 51.25%
[34 empty] | 3.62 | PS 600 | 6 | 52.5% | 3.62 | PS 600 | 6 | 52.5% | 3.62 | PS 600 | 6 | 52.5%
[34 empty] | 3.63 | PS 600 | 6 | 53.75% | 3.63 | PS 600 | 6 | 53.75% | 3.63 | PS 600 | 6 | 53.75%
[34 empty] | 3.64 | PS 600 | 6 | 55% | 3.64 | PS 600 | 6 | 55% | 3.64 | PS 600 | 6 | 55%
[34 empty] | 3.65 | PS 600 | 6 | 56.25% | 3.65 | PS 600 | 6 | 56.25% | 3.65 | PS 600 | 6 | 56.25%
[34 empty] | 3.66 | PS 600 | 6 | 57.5% | 3.66 | PS 600 | 6 | 57.5% | 3.66 | PS 600 | 6 | 57.5%
[34 empty] | 3.67 | PS 600 | 6 | 58.75% | 3.67 | PS 600 | 6 | 58.75% | 3.67 | PS 600 | 6 | 58.75%
[34 empty] | 3.68 | PS 600 | 6 | 60% | 3.68 | PS 600 | 6 | 60% | 3.68 | PS 600 | 6 | 60%
[34 empty] | 3.69 | PS 600 | 6 | 61.25% | 3.69 | PS 600 | 6 | 61.25% | 3.69 | PS 600 | 6 | 61.25%
[34 empty] | 3.7 | PS 600 | 6 | 62.5% | 3.7 | PS 600 | 6 | 62.5% | 3.7 | PS 600 | 6 | 62.5%
[34 empty] | 3.71 | PS 600 | 6 | 63.75% | 3.71 | PS 600 | 6 | 63.75% | 3.71 | PS 600 | 6 | 63.75%
[34 empty] | 3.72 | PS 600 | 6 | 65% | 3.72 | PS 600 | 6 | 65% | 3.72 | PS 600 | 6 | 65%
[34 empty] | 3.73 | PS 600 | 6 | 66.25% | 3.73 | PS 600 | 6 | 66.25% | 3.73 | PS 600 | 6 | 66.25%
[34 empty] | 3.74 | PS 600 | 6 | 67.5% | 3.74 | PS 600 | 6 | 67.5% | 3.74 | PS 600 | 6 | 67.5%
[34 empty] | 3.75 | PS 600 | 6 | 68.75% | 3.75 | PS 600 | 6 | 68.75% | 3.75 | PS 600 | 6 | 68.75%
[34 empty] | 3.76 | PS 600 | 6 | 70% | 3.76 | PS 600 | 6 | 70% | 3.76 | PS 600 | 6 | 70%
[34 empty] | 3.77 | PS 600 | 6 | 71.25% | 3.77 | PS 600 | 6 | 71.25% | 3.77 | PS 600 | 6 | 71.25%
[34 empty] | 3.78 | PS 600 | 6 | 72.5% | 3.78 | PS 600 | 6 | 72.5% | 3.78 | PS 600 | 6 | 72.5%
[34 empty] | 3.79 | PS 600 | 6 | 73.75% | 3.79 | PS 600 | 6 | 73.75% | 3.79 | PS 600 | 6 | 73.75%
[34 empty] | 3.8 | PS 600 | 6 | 75% | 3.8 | PS 600 | 6 | 75% | 3.8 | PS 600 | 6 | 75%
[34 empty] | 3.81 | PS 600 | 6 | 76.25% | 3.81 | PS 600 | 6 | 76.25% | 3.81 | PS 600 | 6 | 76.25%
[34 empty] | 3.82 | PS 600 | 6 | 77.5% | 3.82 | PS 600 | 6 | 77.5% | 3.82 | PS 600 | 6 | 77.5%
[34 empty] | 3.83 | PS 600 | 6 | 78.75% | 3.83 | PS 600 | 6 | 78.75% | 3.83 | PS 600 | 6 | 78.75%
[34 empty] | 3.84 | PS 600 | 6 | 80% | 3.84 | PS 600 | 6 | 80% | 3.84 | PS 600 | 6 | 80%
[34 empty] | 3.85 | PS 600 | 6 | 81.25% | 3.85 | PS 600 | 6 | 81.25% | 3.85 | PS 600 | 6 | 81.25%
[34 empty] | 3.86 | PS 600 | 6 | 82.5% | 3.86 | PS 600 | 6 | 82.5% | 3.86 | PS 600 | 6 | 82.5%
[34 empty] | 3.87 | PS 600 | 6 | 83.75% | 3.87 | PS 600 | 6 | 83.75% | 3.87 | PS 600 | 6 | 83.75%
[34 empty] | 3.88 | PS 600 | 6 | 85% | 3.88 | PS 600 | 6 | 85% | 3.88 | PS 600 | 6 | 85%
[34 empty] | 3.89 | PS 600 | 6 | 86.25% | 3.89 | PS 600 | 6 | 86.25% | 3.89 | PS 600 | 6 | 86.25%
[34 empty] | 3.9 | PS 600 | 6 | 87.5% | 3.9 | PS 600 | 6 | 87.5% | 3.9 | PS 600 | 6 | 87.5%
[34 empty] | 3.91 | PS 600 | 6 | 88.75% | 3.91 | PS 600 | 6 | 88.75% | 3.91 | PS 600 | 6 | 88.75%
[34 empty] | 3.92 | PS 600 | 6 | 90% | 3.92 | PS 600 | 6 | 90% | 3.92 | PS 600 | 6 | 90%
[34 empty] | 3.93 | PS 600 | 6 | 91.25% | 3.93 | PS 600 | 6 | 91.25% | 3.93 | PS 600 | 6 | 91.25%
[34 empty] | 3.94 | PS 600 | 6 | 92.5% | 3.94 | PS 600 | 6 | 92.5% | 3.94 | PS 600 | 6 | 92.5%
[34 empty] | 3.95 | PS 600 | 6 | 93.75% | 3.95 | PS 600 | 6 | 93.75% | 3.95 | PS 600 | 6 | 93.75%
[34 empty] | 3.96 | PS 600 | 6 | 95% | 3.96 | PS 600 | 6 | 95% | 3.96 | PS 600 | 6 | 95%
[34 empty] | 3.97 | PS 600 | 6 | 96.25% | 3.97 | PS 600 | 6 | 96.25% | 3.97 | PS 600 | 6 | 96.25%
[34 empty] | 3.98 | PS 600 | 6 | 97.5% | 3.98 | PS 600 | 6 | 97.5% | 3.98 | PS 600 | 6 | 97.5%
[34 empty] | 3.99 | PS 600 | 6 | 98.75% | 3.99 | PS 600 | 6 | 98.75% | 3.99 | PS 600 | 6 | 98.75%
[34 empty] | 4 | PS 600 | 6 | 100% | 4 | PS 600 | 6 | 100% | 4 | PS 600 | 6 | 100%
[34 empty] | 4.01 | N/A | N/A | N/A | 4.01 | N/A | N/A | N/A | 4.01 | N/A | N/A | N/A
[34 empty] | 100 | N/A | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A | N/A | N/A

## REVISION (hidden)
REV | DATE | COMMENTS
3.0 | 2012-03-01 | Added sizes 410, 340, and 360. Also changed the round up decimal to .9 from .8.
4.0 | 2012-12-19 | Changed to maximize added rubber. Added alternate calc for if less than min rqd links. Changed to .9 round up.
4D | 2013-08-27 | Changed table so that will not recommend model 600 even if gap too large.
4E | 2014-08-04 | Changed to include a check for when 4 links is first recommended. Must also then pass rule of thumb that annular space must be <1" for pipe diameters <6".
5 | 2015-06-15 | Changed min # of links to follow new information from Linkseal, based on model #. Also a new acceptabillity check based on the same table for min and max Ods for the pipes.

## DIAMETERS (hidden)
| ODs |  |  |  | ID
NOMINAL DIA | STEEL / PVC OD | IRON (EXTRA HEAVY) OD | IRON (SERVICE WEIGHT) OD | DUCTILE IRON OD | STEEL SLEEVE ID
0.5 | 0.84 | NOT AVAIL | NOT AVAIL | NOT AVAIL | NOT AVAIL
0.75 | 1.05 | NOT AVAIL | NOT AVAIL | NOT AVAIL | NOT AVAIL
1 | 1.315 | NOT AVAIL | NOT AVAIL | NOT AVAIL | NOT AVAIL
1.25 | 1.66 | NOT AVAIL | NOT AVAIL | NOT AVAIL | NOT AVAIL
1.5 | 1.9 | NOT AVAIL | NOT AVAIL | NOT AVAIL | NOT AVAIL
2 | 2.375 | 2.38 | 2.3 | 2.5 | 2.067
2.5 | 2.875 | NOT AVAIL | NOT AVAIL | NOT AVAIL | 2.469
3 | 3.5 | 3.5 | 3.3 | 3.96 | 3.068
3.5 | 4 | NOT AVAIL | NOT AVAIL | NOT AVAIL | 3.548
4 | 4.5 | 4.5 | 4.3 | 4.8 | 4.026
5 | 5.563 | 5.5 | 5.3 | NOT AVAIL | 5.047
6 | 6.625 | 6.5 | 6.3 | 6.9 | 6.065
8 | 8.625 | 8.62 | 8.38 | 9.05 | 7.981
10 | 10.75 | 10.75 | 10.5 | 11.1 | 10.02
12 | 12.75 | 12.75 | 12.5 | 13.2 | 12
14 | 14 | NOT AVAIL | NOT AVAIL | 15.3 | 13.25
15 | NOT AVAIL | 15.88 | 15.62 | NOT AVAIL | NOT AVAIL
16 | 16 | NOT AVAIL | NOT AVAIL | 17.4 | 15.25
18 | 18 | NOT AVAIL | NOT AVAIL | 19.5 | 17.25
20 | 20 | NOT AVAIL | NOT AVAIL | 21.6 | 19.25
22 | 22 | NOT AVAIL | NOT AVAIL | NOT AVAIL | 21.25
24 | 24 | NOT AVAIL | NOT AVAIL | 25.8 | 23.25
26 | 26 | NOT AVAIL | NOT AVAIL | NOT AVAIL | 25.25
28 | 28 | NOT AVAIL | NOT AVAIL | NOT AVAIL | 27.25
30 | 30 | NOT AVAIL | NOT AVAIL | 32 | 29.25
32 | 32 | NOT AVAIL | NOT AVAIL | NOT AVAIL | 31.25
34 | 34 | NOT AVAIL | NOT AVAIL | NOT AVAIL | 33.25
36 | 36 | NOT AVAIL | NOT AVAIL | 38.3 | 35.25
42 | 42 | NOT AVAIL | NOT AVAIL | 44.5 | 41.25
48 | 48 | NOT AVAIL | NOT AVAIL | 50.8 | 47.25
54 | NOT AVAIL | NOT AVAIL | NOT AVAIL | NOT AVAIL | 53.25